## SGF_Parameters
SGF1_lvttoc | SGF1_ptoc1_lvttoc | SGF2_ptoc1_lvttoc | SGF3_ptoc1_lvttoc | SGF4_ptoc1_lvttoc | SGF5_ptoc1_lvttoc | SGF6_ptoc1_lvttoc | SGF1_ptoc2_lvttoc | SGF2_ptoc2_lvttoc | SGF3_ptoc2_lvttoc | SGF4_ptoc2_lvttoc | SGF5_ptoc2_lvttoc | SGF6_ptoc2_lvttoc | SGF1_ptoc3_lvttoc | SGF2_ptoc3_lvttoc | SGF3_ptoc3_lvttoc | SGF4_ptoc3_lvttoc | SGF5_ptoc3_lvttoc | SGF6_ptoc3_lvttoc | SGF1_ptuv1_lvttoc | SGF1_phar1_lvttoc | SGF1_rblc1_lvttoc | SGF1_lvrbvtr1 | SGF2_lvrbvtr1 | SGF1_ptrc1_tofflvlgc | SGF1_rbre1_tofflvlgc | SGF2_rbre1_tofflvlgc | SGF3_rbre1_tofflvlgc | SGF1_rblc1_tofflvlgc | SGF2_rblc1_tofflvlgc | SGF3_rblc1_tofflvlgc | SGF1_lvalv | SGF2_lvalv | SGF3_lvalv | SGF4_lvalv | SGF5_lvalv | SGF6_lvalv | SGF7_lvalv | SGF8_lvalv | SGF9_lvalv | SGF10_lvalv | SGF1_ptoc1_lvarctoc | SGF2_ptoc1_lvarctoc | SGF1_ptrc1_ttoclgc | SGF2_ptrc1_ttoclgc | SGF3_ptrc1_ttoclgc | Номинальный ток входа
0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5

## Settings
T1_ptoc1_lvttoc | Iset_ptoc1_lvttoc | Icoarse_ptoc1_lvttoc | T1_ptoc2_lvttoc | Iset_ptoc2_lvttoc | Icoarse_ptoc2_lvttoc | T1_ptoc3_lvttoc | Iset_ptoc3_lvttoc | Icoarse_ptoc3_lvttoc | Uop_ptuv1_lvttoc | U2op_ptuv1_lvttoc | Imax_phar1_lvttoc | Ratio_phar1_lvttoc | Umin_lvrbvtr1 | U2max_lvrbvtr1 | T1_lvrbvtr1 | Iset_ptoc1_lvarctoc
1 | 0.2 | 0.6 | 1 | 0.2 | 0.6 | 1 | 0.2 | 0.6 | 50 | 15 | 1 | 40 | 50 | 15 | 1 | 1

## Inputs
VYVOD | OV_lvttoc | OVst_ptoc1 | OVst_ptoc2 | OVst_ptoc3 | NaSign_ptoc1 | NaSign_ptoc2 | NaSign_ptoc3 | SV1vkl | IA | dIA | IB | dIB | IC | dIC | UA1 | dUA1 | UB1 | dUB1 | UC1 | dUC1 | IA2harm | IB2harm | IC2harm | KPONvnesh_ptuv1 | VNN1vkl | OV_lvrbvtr1 | vnesh_bnn_srab_lvrbvtr1 | OVlot | OVlo | OVzapv | OVzavr
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 240 | 2 | 120 | 58 | 0 | 58 | 240 | 58 | 120 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Outputs
vvod_lvrbvtr1 | oper_vyvod_lvrbvtr1 | u_lin_pusk_lvrbvtr1 | u2_pusk_lvrbvtr1 | pusk_lvrbvtr1 | neispr_zn_lvrbvtr1 | vvod_ptoc1_lvttoc | oper_vyvod_ptoc1_lvttoc | mtzA_pusk_ptoc1_lvttoc | mtzB_pusk_ptoc1_lvttoc | mtzC_pusk_ptoc1_lvttoc | gen_pusk_ptoc1_lvttoc | mtz_srabsign_ptoc1_lvttoc | mtz_srab_ptoc1_lvttoc | io_A_ptoc1_lvttoc | io_B_ptoc1_lvttoc | io_C_ptoc1_lvttoc | vvod_ptoc2_lvttoc | oper_vyvod_ptoc2_lvttoc | mtzA_pusk_ptoc2_lvttoc | mtzB_pusk_ptoc2_lvttoc | mtzC_pusk_ptoc2_lvttoc | gen_pusk_ptoc2_lvttoc | mtz_srabsign_ptoc2_lvttoc | mtz_srab_ptoc2_lvttoc | io_A_ptoc2_lvttoc | io_B_ptoc2_lvttoc | io_C_ptoc2_lvttoc | vvod_ptoc3_lvttoc | oper_vyvod_ptoc3_lvttoc | mtzA_pusk_ptoc3_lvttoc | mtzB_pusk_ptoc3_lvttoc | mtzC_pusk_ptoc3_lvttoc | gen_pusk_ptoc3_lvttoc | mtz_srabsign_ptoc3_lvttoc | mtz_srab_ptoc3_lvttoc | io_A_ptoc3_lvttoc | io_B_ptoc3_lvttoc | io_C_ptoc3_lvttoc | kpon_pusk_ptuv1_lvttoc | ia_start_out_phar1_lvttoc | ib_start_out_phar1_lvttoc | ic_start_out_phar1_lvttoc | start_phar1_lvttoc | blok_rblc1_lvttoc | mtz_pusk_lvttoc | vvod_ptrc1 | oper_vyvod_ptrc1 | pusk_ptrc1 | srab_ptrc1 | vvod_rblc1 | oper_vyvod_rblc1 | zapret_rblc1 | vvod_rbre1 | oper_vyvod_rbre1 | zapret_rbre1 | pusk_lvalv | pusk_ptoc1_lvarctoc | pusk_ptrc1_ttoclgc | IAB | dIAB | IBC | dIBC | ICA | dICA | I2 | I0 | I1 | UAB_ptuv1 | UBC_ptuv1 | UCA_ptuv1 | U2_ptuv1 | U0_ptuv1 | U1_ptuv1
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 2.0 | 30.0 | 2.0 | -90.0 | 2.0 | 150.0 | 0.0 | 0.0 | 2.0 | 100.46 | 100.46 | 100.46 | 0.0 | 0.0 | 58.0